## Cover Page
Cause No. 45744
Southern Indiana Gas and Electric Company d/b/a CenterPoint Energy Indiana South
CEI South Exh. 1
FILED
2022-07-22
INDIANA UTILITY
REGULATORY COMMISSION

## Report
IC 8-1-8.5-13(i) Reporting Form - Planning Resource Year 2 (2022 to 2023) | [6 empty] | CenterPoint Energy (CEI South)
Indiana Utility Regulatory Commission
Add rows below as necessary. For resources located outside of Zone 6, please provide a description of the deliverability arrangements.
For demand response resources, please provide a description of each program.
| Owned Resource IC 8-1-8.5-13(i)(1) definition | ICAP (MW) Nameplate capacity | Summer UCAP (MW) IC 8-1-8.5-13(f) definition | Winter UCAP (MW) IC 8-1-8.5-13(g) definition | Location: RTO interconnection zone | Fuel Source | Additional Comments
| AB Brown 1 | 245 | 239.2 | 236.7 | MISO Zone 6 | Coal | For all thermal resources, summer is assumed to be June-August and winter is assumed to be December-February. Seasonal UCAP calculated using annual GVTC results and XEFORd values specific to each season.
| AB Brown 2 | 240 | 224.7 | 227.6 | MISO Zone 6 | Coal | -
| AB Brown 3 | 80 | 74.7 | 74.5 | MISO Zone 6 | Gas/Fuel Oil | Primary fuel is natural gas but can operate on fuel oil
| AB Brown 4 | 80 | 59.4 | 66 | MISO Zone 6 | Gas | -
| FB Culley 2 | 90 | 83.5 | 87.9 | MISO Zone 6 | Coal | -
| FB Culley 3 | 270 | 265.2 | 260.8 | MISO Zone 6 | Coal | -
| Warrick 4 | 150 | 138.3 | 134.7 | MISO Zone 6 | Coal | Jointly owned 300MW unit that is operated by Alcoa. CEI South owns 50%.
| OVEC (Ohio Valley Electric Corp.) | 32.2 | 29.8 | 30.9 | MISO External Zone 23 | Coal | CEI South owns 1.5% share of OVEC's total capacity. OVEC is located in MISO external zone 23, and is interconnected through the transmission provider LGEE (Louisville Gas & Electric) to SIGE with Transmission Service Request reference #88106335.
| Troy Solar | 50 | 36.4 | 0.44618 | MISO Zone 6 | Solar | Summer UCAP based on first year's operation data. Winter UCAP based on first year's operational data and MISO's proposed accreditation in seasonal construct.
| Oak Hill Solar | 2 | 0 | 0 | MISO Zone 6 | Solar | Located on CEI South distribution system and accounted for in peak load forecast. Not a UCAP resource.
| Volkman Rd Solar | 2 | 0 | 0 | MISO Zone 6 | Solar | Located on CEI South distribution system and accounted for in peak load forecast. Not a UCAP resource.
| Volkman Road Battery | 1 | 0 | 0 | MISO Zone 6 | Battery | Located on CEI South distribution system and accounted for in peak load forecast. Not a UCAP resource.
| Blackfoot Landfill | 3.2 | 0 | 0 | MISO Zone 6 | Landfill Gas | Located on CEI South distribution system and accounted for in peak load forecast. Not a UCAP resource.
| Contracted Resource IC 8-1-8.5-13(i)(2) definition | ICAP (MW) Nameplate capacity | Summer UCAP (MW) IC 8-1-8.5-13(f) definition | Winter UCAP (MW) IC 8-1-8.5-13(g) definition | Location: RTO interconnection zone | Fuel Source | Additional Comments
| Benton County Wind Farm | 29.5 | 2.2 | 7.375 | MISO Zone 6 | Wind | Winter accreditation uses MISO LOLE average wind ELCC from Dec.-Feb. to determine accreditation | https://cdn.misoenergy.org/PY%202022-23%20LOLE%20Study%20Report601325.pdf
| Fowler Wind Farm | 50 | 3.9 | 12.5 | MISO Zone 6 | Wind | Winter accreditation uses MISO LOLE average wind ELCC from Dec.-Feb. to determine accreditation
| Demand Response Resource IC 8-1-8.5-13(i)(3) definition | Summer UCAP (MW) IC 8-1-8.5-13(f) definition | Winter UCAP (MW) IC 8-1-8.5-13(g) definition | Additional Comments
| DR - DLC - Summer Cycler | 8.7 | 0 | Direct load control via switches on electric cooling units and electric water heaters. This DR is only available in summer months per CEI South tariff
| RTO established Planning Reserve Margin requirement (see IC 8-1-8.5-13 (i)(4) | Summer Demand 1022.7MWx(1+ % PRM 8.7%)x(1+%Transmission Loss 2.4%) = 1138.4MW
| Please describe any other federal reliability requirement: | -
Reliability Adequacy Metrics [defined in IC 8-1-8.5-13(e)]
| Summer RA Metric IC 8-1-8.5-13(e)(1) | Winter RA Metric IC 8-1-8.5-13(e)(2)
| Summer UCAP/PRM Requirement = 102% | Winter UCAP/PRM Requirement = 128.8%
| Summer PRMR | Winter PRMR
| 1138.3551 | 884.8767
| SUMMER TOTAL UCAP | WINTER TOTAL UCAP
| 1166 | 1139.4212
| Summer RA Metric (%) | Winer RA Metric (%)
| 102.4% | 128.8%

## Winter PRMR Calculation
2022-2023 Coincident Peak (Summer) | 95.69%
2022-2023 PRM | 8.7%
Transmission Losses | 2.4%
Load
2022-2023 MISO PY Winter Load Forecast (With Transmission Losses) | 851.2103
Coincident Peak With Transmission Losses | 814.5232
Transmission Losses | 19.5486
Demand Forecast (Coincident Peak Without Transmission Losses) | 794.9746
Effective PRM | 69.1628
PRMR Without Transmission Losses | 864.1374
Transmission Losses | 20.7393
Winter PRMR With Transmission Losses | 884.8767
Note: Projected winter peak load and summer coincidence factor used to calculate winter PRMR